Product Engineering Sheet

Engineering Specification for a System Based Control Module for a

# Combustible Gas Sensing Element

GENERAL DESCRIPTION

The Module shall utilize a catalytic bead sensor as the gas sensing element. The Module shall be capable of displaying gas concentrations within the range of 0 to 100% of the Lower Flammable Limit (LFL) or Lower Explosive Limit (LEL). The Module shall generate a 4 to 20mA signal that shall be proportional to the 0 to 100% of full scale indication for the range in use listed above and be capable of operating normally with a total loop resistance up to 500 ohms. A test feature shall be included and be capable of testing the front and rear panel indicators and outputs by simulating an increasing presence of gas from 0 to 100% of full scale. The user shall have the option of activating or inhibiting the alarm outputs through a software selection. The Module shall be rated for use in non-hazardous areas.

ALARM INDICATIONS AND OUTPUTS

Each Module shall have two alarm levels. The alarm levels shall be user specified in increments of 5% LEL from 5 to 60% of full scale. There shall be a high-visibility front panel LED (red) associated with each level of alarm. There shall be an Open Collector Output associated with each level of alarm and be capable of sinking 100mA @ 30VDC. The alarm relays shall have two sets of normally open contacts and two sets of normally closed contacts capable of 4A @ 250VAC and 3A @ 30VDC. Software selectable alarm options consisting of Energized/De-Energized, Latching/Non-Latching and the Alarm Set Point shall be available for each alarm level. The Front Panel LED indicators shall have Open Collector outputs associated with each alarm level for remote visual indications of the alarm levels.

MALFUNCTION INDICATIONS AND OUTPUTS

The malfunction indications and outputs shall consist of:

- Remote analog signal indication of 0mA

- High-visibility front panel LED (amber) indicator

- Open collector output

- Normally open relay contacts

- Normally closed relay contacts

The malfunction conditions that are monitored shall be:

- Low DC supply voltage

- Sensor errors

- Calibration errors

- Program errors

- Hardware errors

ELECTRICAL SPECIFICATIONS

The input power shall be a nominal 24 VDC with a range of 20 to 35 VDC. The current requirement shall be no greater than 300mA.

WARRANTY

This unit shall have a two-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.

ENVIRONMENTAL SPECIFICATIONS

This unit shall be capable of operation within a temperature range of 0° F to 150° F (-18° C to +66° C) and a humidity range of 5% to 100% relative humidity, non-condensing.