Product Engineering Sheet

Engineering Specification for an Open Path Infrared

Hydrocarbon Gas Monitoring System

# GENERAL DESCRIPTION

The open path infrared gas monitoring system shall consist of an infrared source and a microprocessor based IR receiver unit. This system will measure gas concentrations by an IR method based on absorption of IR radiation as it passes through a volume of gas. The gas to be measured must be infrared active like hydrocarbons and the corresponding output of the system will be expressed in both 0-5 LEL·meter and 0-5000 ppm·meter (methane) or 0-1 LEL·meter and 0-2000 ppm·meter (propane).

SYSTEM SPECIFICATIONS

The system shall have two independent measurement ranges of 0 to 5 LEL·meter and 0 to 5000 ppm·meter of methane or 0 to 1 LEL·meter and 0 to 2000 ppm·meter (propane). Path length shall be 5 to 150 meters (16 to 492 ft) from source to receiver, with product configurations for 5 to 30 meters (16 to 98 ft), 20 to 100 meters (66 to 328 ft), and 80 to 150 meters (262 to 492 ft). The system shall be able to measure ppm·m and LEL·m concentrations using a single 4 – 20 mA analog output signal by dividing the analog range between 4 and 20 mA into two scales (split range mode). Response time when exposed to full scale gas concentration shall be T90 < 3 seconds. System repeatability shall be (5% of last reading for each scale. No traditional routine calibration shall be required. Alignment will be performed without opening the enclosure. The warranty on the system shall be two years. The system must have three specific modes of operation for applying a test gas, selection of user defined options, and alignment of the source and receiver. The system shall be designed to meet certifications for CSA Class I, Division 1 & 2, Groups B, C, and D; Class II, Div. 1 & 2, Groups E, F, and G; Class III; and ATEX Class I, Zone 1, IIB+H2; II 2 G D, Ex d IIB+H2 T4 Gb Ex tb IIIC T135°C Db.

MECHANICAL SPECIFICATIONS

Housing size for the IR source and receiver units shall be:

Source: 		5.3” Dia x 12.4” Length (135 mm Dia. x 315 mm Length)

Receiver: 	5.3” Dia x 12.4” Length (135 mm Dia. x 315 mm Length)

The enclosure material shall be 316 stainless steel. Weight for the system components shall be:

Source: 		12.2 lbs (5.53 kg)

Receiver: 	12.34 lbs (5.6 kg)

There shall be two conduit entries supplied with ¾” NPT or M25 x 1.5-6H.

ELECTRICAL SPECIFICATIONS

The operating voltage shall be 24 VDC nominal with a range of 20-36 VDC.

Power consumption for the system shall be:

Source: 		24 VDC @ 12 W (max.) with relays

Receiver: 	24 VDC @ 10 W (max.) with relays, 24 VDC @ 5 W (max.) with no relays, no heater

Standard alarm outputs shall include two (2) 4-20 mA signals (600 ohm load max.) and four (4) SPDT relays as follows:

0-5000 ppm∙meter	0-5 LEL∙meter

0 mA*		Startup/Fault 	Startup/Fault

1.5 mA*		Test Gas/Setup 	Test Gas/Setup

2 mA*		Beam Block		Beam Block

4-20 mA		0-5000 ppm∙m	0-5 LEL∙m

4-12 mA***	0-5000 ppm∙m	-----------

12-20 mA***	-----------		0-5 LEL∙m

21.7 mA 		Over-range	Over-range

Relays shall be four (4) SPDT, 8 amperes @ 30 VDC resistive max.; 250 VAC; ppm·meter Alarm, LEL·meter Warning, LEL·meter Alarm and Fault.

Relay options shall be software selectable for:

Latching/Non-Latching Warning and Alarm

Energized/De-Energized Warning and Alarm

Warning & Alarm level set-points set in 0.5 LEL·meter (0.2 LEL·meter) increments from 2.0 to 4.5 LEL·meter and 500 ppm·meter (0.8 to 1.8 LEL·meter and 200 ppm·meter) increments from 2000 to 4500 ppm·meter (800 to 1800 ppm·meter). The IR receiver unit shall have a two digit, seven segment digital display which automatically changes ranges between ppm·meter and LEL·meter scales. In addition, a LED indication of scale displayed shall be present.

The system shall have fault diagnostics and fault codes (F0-F11) shall be displayed on the digital display for specific fault indication):

F0 – Excessive negative drift or high IR

F1 – Partial beam block or dirty lens

F2 – Alignment

F3 – Beam block

F4 – Not used

F5 – Setup menu

F6 – Low supply voltage

F7 – Heater

F8 – Failed zeroing

F9 – Gas left

F10 – Reset short

F11 – Unit overheating

tF7 – Source internal failure

The system shall be certified to CSA, ATEX, IECEx and FM standards and have the CE Marking. The device shall also be IEC 61508 certified to SIL 3. The optical path will be continuously tested for beam block (100% block) and will indicate a fault if blocked for longer than 30 seconds. The system shall have an automatic gain control which will adjust for signal reduction of the reference wavelength. The system shall provide a field background zero adjustment.

ENVIRONMENTAL SPECIFICATIONS

The operating temperature of the system shall be -67°F to +149°F (-55°C to +65°C). The operating humidity range of the system shall be 0 to 95% RH, non-condensing. The system must meet the performance requirements of FM 6325, EN 50241-1, -2, and IEC 60079-29-4.  The system shall have a weatherproof rating of Type 4X, IP66/67.

# Text boxes

* HART units can be configured to never output current less than 3.5 mA if the host equipment is incapable of working below this level.

** 0 to 2000 ppm•meter and 0 to 1 LEL•meter on propane unit.

*** Using optional split range