Product Engineering Sheet

Engineering Specification for a System Based Display Module for a

Combustible Gas Smart Sensing and Transmitting Unit

GENERAL DESCRIPTION

The Display Module shall be capable of receiving a 0 to 20mA signal from the Combustible Gas Sensing and Transmitting Unit and transmitting a 0 to 20mA signal to a remote device. The Display Module shall be capable of displaying gas concentrations within the range of 0 to 99% of the Lower Flammable Limit (LFL) or Lower Explosive Limit (LEL). The 4 to 20mA received from the Field device and retransmitted from the Display Module shall be proportional to the 0 to 99% of full scale indication listed above. A remote test feature shall be included and be capable of testing the front and rear panel indicators and outputs by simulating an increasing presence of gas from 0 to 100% of full scale. The Display Module shall be rated for use in non-hazardous areas.

ALARM INDICATIONS AND OUTPUTS

Each Display Module shall have 2 alarm levels. The alarm levels shall be user or field specified in increments of 5% LEL from 5 to 60% of full scale. There shall be a high-visibility front panel LED (red) associated with each level of alarm. There shall be an Open Collector Output associated with each level of alarm and be capable of sinking 100mA @ 30VDC. Two DPDT Alarm relays shall be present. The alarm relays shall have two sets of normally open contacts and two sets of normally closed contacts capable of 4A @ 250VAC and 3A @ 30VDC. Software selectable alarm options consisting of Energized/De-Energized and Latching/Non-Latching shall be available for each alarm level. The Front Panel LED indicators shall have Open Collector outputs associated with each alarm level for remote visual indications of the alarm levels.

MALFUNCTION INDICATIONS AND OUTPUTS

The malfunction indications and outputs shall consist of:

- Remote analog signal indication of 0mA

- High-visibility front panel LED (amber) indicator

- Open Collector output

- A set of normally open and normally closed SPDT relay contacts

The malfunction conditions that are monitored shall be:

- Low DC supply voltage

- Sensing and Transmitter faults

- Hardware/Software watchdogs

- Inhibit Mode (user selectable)

- Card Test (user selectable).

ELECTRICAL SPECIFICATIONS

The input power shall be a nominal 24 VDC with a range of 20 to 35 VDC. The current requirement shall be no greater than 475mA with Smart Sensor. The input impedance of the Display Module for the input signal shall not exceed 30 ohms.

WARRANTY

This unit shall have a two-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.

ENVIRONMENTAL SPECIFICATIONS

This unit shall be capable of operation within a temperature range of 0°F to 150°F (-18°C to +66°C) and a humidity range of 5% to 100% relative humidity, non-condensing.