Product Engineering Sheet

Engineering Specification for a System Based Display Module for a

Flame Detecting and Transmitting Unit

# GENERAL DESCRIPTION

The Display Module shall be capable of receiving a 0 to 20mA signal from the Flame Detecting and Transmitting Unit and transmitting a 0 to 20mA signal to a remote device. The Display Module shall be capable of indicating the presence of flame radiation. The 4 to 20mA received and transmitted from the Display Module shall be capable of operating normally with a total loop resistance up to 300 ohms. A remote test feature shall be included and be capable of testing the front and rear panel indicators and outputs by simulating an increasing hazard. The user shall have the option of activating or inhibiting the alarm outputs through a software selection. The Display Module shall be rated for use in non-hazardous areas.

ALARM INDICATIONS AND OUTPUTS

Each Display Module shall have two alarm levels, one shall be Immediate and the other shall be Time Delayed.

The alarm time delay shall be user specified at one of the following constants:

- 1 Second

- 2 Seconds

- 4 Seconds

- 8 Seconds

There shall be a high-visibility front panel LED (red) associated with each level of alarm. There shall be an open collector output associated with each level of alarm and be capable of sinking 100mA @ 30 VDC. Software selectable alarm options consisting of Energized/De-Energized and Latching/Non-Latching shall be available for each alarm level. The Front Panel LED indicators shall have open collector outputs associated with each alarm level for remote visual indications of the alarm levels.

MALFUNCTION INDICATIONS AND OUTPUTS

The malfunction indications and outputs shall consist of:

- Remote analog signal indication of 0mA

- High-visibility front panel LED (amber) indicator

- Open collector output

- Optional set of normally open and normally closed relay contacts

The malfunction conditions that are monitored shall be:

- Low DC supply voltage

- Detecting and Transmitter faults

ELECTRICAL SPECIFICATIONS

The input power shall be a nominal 24 VDC with a range of 20 to 35 VDC. The current requirement shall be no greater than 425mA including detector. The input impedance of the Display Module for the input signal shall not exceed 30 ohms.

ENVIRONMENTAL SPECIFICATIONS

This unit shall be capable of operation within a temperature range of 0° F to 150° F (-18°C to +66°C) and a humidity range of 5% to 100% relative humidity, non-condensing.

WARRANTY

This unit shall have a two-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.