Product Engineering Sheet

Engineering Specification for a Hydrogen Sulfide

Intelligent Sensing and Transmitting Unit with Relays

GENERAL DESCRIPTION

The Intelligent Sensing and Transmitting Unit shall contain microprocessor-based electronics, field connection terminations, dual-redundant Modbus or HART and three 8A relays in a single explosion-proof housing. The sensing element shall be of the diffusion, adsorption, metal oxide semiconductor (MOS) type. This unit shall be available with a 3-digit digital display window in the cover. This unit shall be capable of one-person calibration. The transmitter shall be capable of interfacing with industrial equipment that can receive a 4 to 20 mA signal. The complete unit must be approved by the Canadian Standards Association (CSA), Factory Mutual (FM), Sira (for ATEX) and have the CE mark. This unit shall be capable of operating in Class I, Division 1, Groups B, C or D and Class 1, Zone 1, Group IIB+H2, T6, hazardous classified locations for CSA and FM approvals and Ex d IIB+H2, T5 (II 2 G) for ATEX approval. The unit will be HART registered and compatible with Emerson Process Management’s AMS Intelligent Device Manager. Further, the detector shall be suitable for SIL 2 and 3 environments.

SENSOR SPECIFICATIONS

The semiconductor sensor shall be suitable for detecting and measuring the concentration of hydrogen sulfide.  It shall have a precision of ±2 ppm or 10% of the applied gas, whichever is greater.  The sensor shall also have a response time (T50) of less than fourteen seconds for screen-covered sensors and less than thirty seconds for sintered sensors. The MOS sensor shall meet the performance standards of ISA 92.0.01 Part 1 – 1998 requirements.

CALIBRATION

This unit shall be capable of calibration without having to de-classify an area and without any adjustments by the operator. Calibration shall be initiated by the application of a magnet to the cover, to an external switch, Modbus command or HART command. Calibration shall be a simple procedure and shall be listed on the cover of the unit.

MALFUNCTION INDICATIONS

The malfunction indications shall be a remote analog signal indication uniquely different than the operational signal and a visible signal to the operator. The malfunction conditions that are monitored shall be:

- Failed Complete Calibration

- Flash Checksum Error

- Sensor Heater Open Error or Sensor Amplifier Error

- Sensor Heater Shorted Error

- Low Supply Voltage

- EEPROM Verification Failure

- Failure to Complete Setup

- Gas Check Period Exceeded

- Switch Error

- Internal Error

# ELECTRICAL SPECIFICATIONS

The input power shall be 24 VDC nominal, 20 to 36 VDC, 350 mA maximum. Three-wire shielded cable (14 to 20 AWG) shall be used for cable runs from the power supply and readout/relay module to the unit. The output signal shall be an analog signal with a range of 0 to 22 mA and a maximum resistance of 650 Ohms. The unit shall be capable of receiving power through cable running up to 2,240 feet from the power supply using 14 AWG wire. The unit shall be capable of transmitting the output signal through the cable up to 8,000 feet to a readout/relay module. The alarm and malfunction relays shall be SPDT contacts with electrical ratings of 8A @ 250 VAC, 8A @ 30 VDC resistive max. The unit shall be equipped with dual Modbus and will be suitable for linking up to 128 units or up to 247 units with repeaters. The unit shall be HART registered.  The HART communication must indicate unit conditions and ppm levels.  It also must be capable of receiving calibration and cal check commands.

ENVIRONMENTAL SPECIFICATIONS

This unit shall be capable of operating within a temperature range of -40°F to +167°F (-40°C to +75°C) for hazardous locations (-40°C to +70°C for ATEX approved installations) and a humidity range of 10% to 95% relative humidity, non-condensing.

WARRANTY

This unit shall have a two-year warranty on the sensing element and on the electronics. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.

SPECIFICATIONS AT A GLANCE

Sensor Type: 		Continuous Adsorption, H2S Specific, Metal Oxide Semiconductor

Sensor Range: 		0 to 20 ppm, 0 to 50 ppm, or 0 to 100 ppm

Repeatability:		± 2 ppm or 10% of applied gas, whichever is greater

Response Time:		T50 < 14 sec (screen), T50 < 30 sec (sintered)

Digital Display: 		Indicates gas concentration, calibration prompts, and (10) fault codes

Electronics: 		Microprocessor-based

Outputs:

A. 	0 to 22 mA analog signal (650 Ohm max. resistance)

0 mA 		Malfunction

1.5 mA 			Gas check

1.5 mA			Setup mode

1.5 mA			Calibrate

4.05 mA ± 0.05mA 	Zero Reading

4 to 20 mA 		0 to 100% LEL

20-22 mA		Over-range

B. 	(2) SPDT Alarm relay contacts, 8A @ 250 VAC, 8A @ 30 VDC res. max.

C. 	(1) SPDT Malfunction relay contact, 8A @ 250 VAC, 8A @ 30 VDC res. max.

Calibration Mode: 	Magnetically initiated, non-intrusive single point with no manual adjustments

Additional Modes:

A. 	Gas check, magnetically initiated, analog signal at 1.5 mA, displays concentration when gas is applied

B. 	Alarm option selections allow for changes in the field:

1. 	Energized or De-Energized

2. 	Latching or Non-Latching

3. 	Alarm Trip Level (Low and High)

Approvals: 	CSA, ATEX, FM approved. CE Marking. HART registered, SIL 2 or 3 suitable

Electrical Classification: 	Class I, Division 1, Groups B, C, & D; Class I, Zone 1, Group IIB+H2

EEx d IIB+H2, T5 II2G

Operating Temperature: 	CSA/FM: 	T6 (Tamb = -40°C to +75°C) hazardous locations

FM: 	T6 (Tamb = -40°C to +60°C) performance

ATEX:   	T5 (Tamb = -40°C to +70°C)

Humidity Range: 	10% to 95% relative humidity, non-condensing

Input Power: 	24 VDC (nominal), 20 to 36 VDC Range, 350 mA max.

Warranty: 	Two years

Cable Requirements: 	Three-wire shielded (14 to 20 AWG)

# Footnotes

The 4 – 20 mA output has a higher safety rating than relay outputs.