Product Engineering Sheet

# Engineering Specifications for a System Based Trip Amplifier/Display Module

# for a Hydrogen Sulfide Smart Sensing and Transmitting Unit

GENERAL DESCRIPTION

The Display Module shall be capable of receiving a 0 to 20mA signal from the H2S Sensing and Transmitting Unit and transmitting a 0 to 20mA signal to a remote device. The Display Module shall be capable of displaying gas concentration within the following ranges of detection:

- 0 to 100 parts-per-million (ppm)

- 0 to 50 ppm

- 0 to 20 ppm

The 4 to 20mA signal received from the Field Device and re-transmitted from the Display Module shall be proportional to the 0 to 100% of full scale indication for the range in use listed above. A remote test feature shall be included and be capable of testing the front panel indicators and rear terminal outputs by simulating an increasing presence of gas from 0 to 100% of full scale. The user shall have the option of activating or inhibiting the rear terminal outputs through a software selection. The Display Module shall be treated for use in non-hazardous areas. All options shall be software selectable by the user.

ALARM INDICATIONS AND OUTPUTS

Each Display Module shall have two alarm levels. The alarm levels shall be user or field specified in increments of one part-per-million from 10 to 95% of full scale. There shall be a high-visibility front panel LED (red) associated with each level of alarm. There shall be an open collector output associated with each level of alarm and be capable of sinking 100mA @ 30VDC. The alarm relays shall be provided as a standard feature and each shall have two sets of normally open contacts and two sets of normally closed contacts capable of 4A @ 250VAC and 3A @ 30VDC. Software selectable alarm options consisting of Energized/De-Energized and Latching/Non-Latching shall be available for each alarm level. The Front Panel LED indicators shall have open collector outputs associated with each alarm level for remote visual indications of the alarm levels.

MALFUNCTION INDICATIONS AND OUTPUTS

The malfunction indications and outputs shall consist of:

- Remote analog signal indication of 0mA

- High-visibility front panel LED (amber) indicator

- Open collector output

- One set of normally open and normally closed relay contacts.

The malfunction conditions that are monitored shall be:

- Low DC supply voltage

- Sensing and Transmitter faults

- Hardware/Software watchdogs

- Inhibit Mode (user selectable)

- Card Test (user selectable)

ELECTRICAL SPECIFICATIONS

The input power shall be a nominal 24 VDC with a range of 20 to 35 VDC. The current requirement shall be no greater than 475mA including the Smart/Intelligent Sensor. The input impedance of the Display Module for the input signal shall not exceed 30 ohms.

ENVIRONMENTAL SPECIFICATIONS

This unit shall be capable of operation within a temperature range of 0° F to 150° F (-18° C to +66° C) and a humidity range of 5% to 100% relative humidity, non-condensing.

WARRANTY

This unit shall have a two-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.