Product Engineering Sheet

Engineering Specification for a 4, 8 or 16 Channel Chassis

# General Description

Each system shall utilize modules capable of monitoring gas sensing elements or a 0 to 20 mA analog signal from gas or flame detection transmitters. The system chassis shall be available in 4, 8 or 16 channel versions with rack or panel mounting options available for each. The 16 channel rack mounted chassis will be compatible with standard 19 inch racks. Each chassis shall contain  a bus for the following independent signals:

- A1 Alarm

- A2 Alarm

- Fault

- Master Accept

- Master Reset

- Unaccept

- CAL

- +24 VDC

- System Common

- Com +

- Com -

Module signals shall be capable of being bussed from one chassis to another (16 channel chassis only), such that 100 modules can comprise a single system. The gas and flame detection modules shall be electrically and physically compatible and capable of being used in the same chassis to form combined fire and gas detection systems.

# Mechanical Specifications

| Rack Mounted | Height | Width | Depth |
| --- | --- | --- | --- |
| 4 Channel | 7.08” (180mm) | 6.1” (155mm) | 9.625” (244mm) |
| 8 Channel | 7.08” (180mm) | 11.1” (257mm) | 9.625” (244mm) |
| 16 Channel | 7.08” (180mm) | 18.1” (460mm) | 9.625” (244mm) |

| Panel Mounted | Height | Width | Depth |
| --- | --- | --- | --- |
| 4 Channel | 9.44” (239.8mm) | 7.24” (184mm) | 9.625” (244mm) |
| 8 Channel | 9.44” (239.8mm) | 11.25” (286mm) | 9.625” (244mm) |
| 16 Channel | 9.44” (239.8mm) | 19.25” (489mm) | 9.625” (244mm) |

# Environmental Specifications

The chassis shall be capable of operating within a temperature range of 0°F to 150°F (-18°C to 66°C). The unit shall operate within a humidity range of 5% to 100% relative humidity, non-condensing.

Electrical Specifications

The system chassis shall be used in safe (non-hazardous) locations. The unit shall comply with CE Marking requirements.

# Warranty

This unit shall have a two-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.