Product Engineering Sheet

Engineering Specification for a System-based

Relay Module

# General Description

The relay module shall be capable of accepting open collector outputs from other Zero Two Series modules and using them as inputs to drive up to four relays. Each set of relays shall have DPDT contacts and have a rating of 4 amps @ 250 VAC / 3 amps @ 30 VDC. Each output shall have a front panel indicator associated with that output (R1, R2, R3, R4). A fault indication shall consist of a front panel indicator (Fault). The relays will activate according to settings that allow the user to select any combination of active Lo/Hi Input/Output for each relay. The relay module shall be electrically and physically compatible with all other modules in the Zero Two Series.

Each system shall utilize modules capable of monitoring gas sensing elements or a 0 to 20 mA analog signal from gas or flame detection transmitters. The system chassis shall be available in 4, 8 or 16 channel versions with rack or panel mounting options available for each. The 16 channel rack mounted chassis will be compatible with standard 19-inch racks. Each chassis shall contain a bus for the following independent signals:

- A1 Alarm

- A2 Alarm

- Fault

- Master Accept

- Master Reset

- Unaccept

- CAL

- +24 VDC

- System Common

- Com +

- Com -

Module signals shall be capable of being bussed from one chassis to another (16 channel chassis only), such that 100 modules can comprise a single system. The gas and flame detection modules shall be electrically and physically compatible and capable of being used in the same chassis to form combined fire and gas detection systems.

# Environmental Specifications

The unit shall be capable of operating within a temperature range of 0°F to 150°F (-18°C to 66°C). The unit shall operate within a humidity range of 5% to 100% relative humidity, non-condensing.

Electrical Specifications

The operating power shall be a nominal 24 VDC with a range of 20-35 VDC. Each set of relays shall have DPDT contacts and have a rating of 4 amps @ 250 VAC / 3 amps @ 30 VDC. The unit shall be used in safe (non-hazardous) locations.

# Warranty

This unit shall have a two-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.