Product Engineering Sheet

Engineering Specification for Toxic Gas Intelligent Sensing and

Transmitting Unit with Optional Relays, HART, and Modbus

GENERAL DESCRIPTION

The Intelligent Sensing and Transmitting Unit shall contain microprocessor-based electronics, field connection terminations, dual-redundant Modbus communications and three 8A relays in a single explosion-proof housing. The sensing element shall be electrochemical diffusion. This unit shall be available with a 3-digit LED display window in the cover. This unit shall be capable of one-person calibration. The transmitter shall be capable of interfacing with industrial equipment that can receive a 4 to 20mA signal. The complete unit must be approved by the Canadian Standards Association (CSA). This unit shall be capable of operating in Class I, Divisions 1 and 2, Groups B, C or D; Class II, Divisions 1 and 2 Groups E, F, & G; Class III; EEx d mb ib IIC + H2 T5, Type 4X with remote interface module.   The unit shall comply with ANSI/ISA-12.13.01-2000 and EN61779-1,-4, HART version 6 registered by HCF, and be compatible with Emerson Process Management’s AMS Intelligent Device Manager.  Further, the detector shall be suitable for SIL 2 environments.

CALIBRATION

This unit shall be capable of calibration without having to de-classify an area and without any adjustments by the operator. Calibration shall be initiated by the application of a magnet to the cover or to an external switch or using MODBUS or HART communication. Calibration shall be a simple procedure and shall be listed on the cover of the unit.

MALFUNCTION INDICATIONS

The malfunction indications shall be a remote analog signal indication separate from operational signals and a visible alpha-numeric fault code signal to the operator. The malfunction conditions that are monitored shall be:

-  Low DC supply voltage

-  Sensor failure

-  Calibration faults

-  Communication fault

- BU EEPROM

- Gas check timeout

-  Setup error

- Calibration check time exceeded

- Switch input error

- RAM Error

# ELECTRICAL SPECIFICATIONS

The input power shall be 24 VDC nominal 0.12 amps, 20 to 36 VDC. Three-wire shielded cable (14 to 22 AWG) shall be used for cable runs from the power supply and controller to the transmitter.  The unit shall be capable of receiving power through 14 AWG cable running up to 3430 feet (1040 meters) from the power supply @ 24VDC nominal (500 Ohm load resistor max). The output shall be an analog signal with a range of 0 to 22 mA.

The optional warn, alarm and malfunction relays shall be integral to the transmitter (not in a separate housing) and will be SPDT contacts with electrical ratings of 8A @ 250VAC, 8A @ 30VDC resistive max. The dual-redundant Modbus communications interface output shall be based on the RS-485 standard and shall allow two-way addressable communications. It will be suitable for linking up to 128 units or up to 247 units with repeaters. The unit shall be HART registered by HCF (HART Communication Foundation).  The HART communication must indicate unit conditions and ppm levels.  It also must be capable of receiving calibration and cal check commands.

WARRANTY

This unit shall have a two-year warranty on the electronics.  The sensor shall have a one-year warranty. The manufacturer shall warrant this unit to be free from defects in workmanship and material under normal use and service within the warranty period from the date of shipment.

ENVIRONMENTAL SPECIFICATIONS

This unit shall be capable of operating within a temperature range of -4°F to +122°F (-20°C to +50°C) for most gasses, and a humidity range of 15% to 90% relative humidity, non-condensing.

Sensor Type: 		Electrochemical, continuous diffusion

Scales:

Gas Formula Range Response Time

Ammonia NH3 0-50 ppm T90<60 sec. 0-100 ppm T90<60 sec.

Carbon Monoxide CO 0-100 ppm T90<30 sec. 0-500 ppm T90<30 sec.

Chlorine Cl2 0-10 ppm T90<60 sec. 0-20 ppm T90<60 sec.

Chlorine Dioxide ClO2 0-3 ppm T90<60 sec.

Hydrogen H2 0-500 ppm T90<30 sec.

Hydrogen Chloride HCl 0-20 ppm T90<100 sec.

Hydrogen Sulfide H2S 0-20 ppm T90<45 sec.

Hydrogen Sulfide H2S 0-50 ppm T90<45 sec.

Hydrogen Sulfide H2S 0-100 ppm T90<45 sec.

Nitric Oxide NO 0-100 ppm T90<10 sec.

Nitrogen Dioxide NO2 0-20 ppm T90<30 sec.

Oxygen O2 0-25% v/v T90<15 sec.

Ozone O3 0-1 ppm T90<90 sec.

Sulfur Dioxide SO2 0-20 ppm T90<10 sec. 0-100 ppm T90<10 sec.

Digital Display: 		Indicates gas concentration, calibration prompts, and fault codes

Electronics: 		Microprocessor-based

Outputs:

A. 	0 to 22 mA analog signal (500 Ohm max. load)

<1.0 mA 	Fault

1.5 mA 	Calibration

1.5 mA		Setup mode

4 mA		Start-up

4 mA +/- 0.2 mA 	Zero Reading

4 to 20 mA 	Detection Range

4 to 22 mA	Signal Range

> 20 mA		Over-range

B. 	(2) SPDT Alarm relay contacts, 8A @ 250 VAC, 8A @ 30 VDC res. max.

C. 	(1) SPDT Malfunction relay contact, 8A @ 250 VAC, 8A @ 30 VDC res. max

Additional Modes:

A. 	Test gas, magnetically initiated, analog signal at 1.5 mA, displays

concentration when gas is applied

B. 	Alarm option selections allow for changes in the field:

1. 	Energized or De-Energized

2. 	Latching or Non-Latching

3. 	Alarm Trip Level

Approvals: 	CSA, ATEX, CE Marking, GOST. HART registered, AMSaware, SIL 2 suitable

Cable Requirements: 	Three-wire shielded (14 to 22 AWG)

Zero Drift:	< 5% per year

Status Indicators:	LED Display w/ gas concentration, Warn and Alarm LEDs, fault and calibration cues, setup options